|  |  |  |  | Name of Meeting Quality, Safety and Improvement Committee. Date of Meeting 20 July 2022. Agenda item: 4.10. |
| --- | --- | --- | --- | --- |
| Health and Safety Report |  |  |  |  |  |  |
| Executive lead: |  | Huw George, Deputy Chief Executive / Executive Director of Operations and Finance |  |  |  |  |
| Author: |  | Chris Orr, Head of Estates and Health and Safety Neil Desmond, Compliance Lead |  |  |  |  |
| Approval/Scrutiny route: |  | Health and Safety Group Business Executive Team (Circulated on 8 July 2022 for information) |  |  |  |  |
| Purpose |  |  |  |  |  |  |
| This report provides an update on the health and safety performance for the period of 01 April 2022 – 30 June 2022. |  |  |  |  |  |  |
| Recommendation: |  |  |  |  |  |  |
| APPROVE | CONSIDER |  | RECOMMEND |  | ADOPT | ASSURANCE |
| The Quality, Safety and Improvement Committee is asked to: - Receive assurance that appropriate measures are in place to monitor compliance and to address areas identified for improvement. |  |  |  |  |  |  |

| Link to Public Health Wales Strategic Plan Public Health Wales has an agreed strategic plan, which has identified seven strategic priorities. This report contributes to the following: |  |
| --- | --- |
| Strategic Priority | Choose an item. All organisational priorities |
| Strategic Priority |  |
| Strategic Priority |  |
| Summary impact analysis |  |
| Equality and Health Impact Assessment | Internal report only |
| Risk and Assurance | The paper details the health and safety risks on Directorate and divisional risk registers and also includes safety alert notifications. It additionally outlines where gaps have been identified, control measures are being implemented to address issues identified.. |
| Health and Care Standards | This report supports and/or takes into account the Health and Care Standards for NHS Wales Quality Themes |
|  | Theme 2 - Safe Care |
| Financial implications | None identified |
| People implications | There are no implications for workforce / staff identified |

# Introduction and Purpose

1.1	The purpose of section one of this report is to provide an update on the health and safety activities and performance for the period 01 April 2022 – 30 June 2022. The key areas of compliance includes;

- Health and safety incidents reported and lessons learnt under the Reporting of Injuries, Diseases and Dangerous Occurrences Regulations (RIDDOR)

- Health and safety premise inspection audits

- Health and safety statutory/mandatory training

- Health and safety Corporate Risk Register

- Notifications and alerts

- Health and safety policies and procedures

The report also provides an update on the specific measures and actions that have been completed or are planned in relation to ensure our estate is compliant with the various legislation and regulations as a result of COVID-19 following the previous update provided in the quarter four report.

- Background

In order for the Health and Safety Group to discharge its responsibilities, it needs to receive assurance that the organisation is effectively managing health and safety. This includes details of any concerns, areas of non-compliance, outstanding actions from relevant health and safety action plans and controls and mitigations are in place.

The Health and Safety Group receives this assurance via this report and exception reports received from the various Directorates/Divisions through the respective Health and Safety leads.

- Key Highlights

3.1 	One RIDDOR was reported during Quarter 1 (01 April 2022 – 30 June 2022). Further details can be found on page 5.

3.2  	Due to the organisation’s response to COVID-19, no health and safety audits have been undertaken within the specified timeframe. As referenced in the Health and Safety work plan, a revised audit will be developed following appointment of the Health and Safety Advisor over the next few months.

3.3 	There are 18 properties within the organisation’s estate portfolio where the responsibility to undertake statutory duties is that of the organisation. These duties include:

- Fire Risk Assessment

- Water Management (Legionella) Risk Assessments

- Electrical Inspection Condition Report (EICR)

- Asbestos survey/re-inspection

- Gas Safety Certification

Currently we are falling short of the 100% compliance target in relation to two areas, namely, electrical inspection condition reports and water management. Further detail is provided at Section 6 on page 5.

3.4 All health and safety alerts and notifications received within the reporting period have been reviewed and addressed, with appropriate actions taken where required.

- Health and Safety Incident Reporting

4.1	Statistics on incident records per directorate

All staff are required to report incidents using the Datix system in accordance with the organisation’s policies and procedures. Incidents are monitored to help identify trends, to ensure investigations are undertaken and are concluded identifying the incident cause and any lessons learnt.

From 01 April 2022 – 30 June 2022, the total number of reported health and safety incidents is provided with a breakdown by directorate shown in Table 1.

Table1. Reported health and safety incidents by Division

| Division | No of incidents |
| --- | --- |
| Local Public Health Teams | 2 |
| Screening | 39 |
| Health Protection | 1 |
| Microbiology | 43 |
| NHS Collaborative | 1 |
| Total | 86 |

All incidents relating to health and safety are notified to the relevant Health and Safety Managers and are followed up. Any learning is captured and shared to prevent reoccurrence.

These incidents are classified under the following categories-

Table 2.  Reported health and safety incidents by category

| Category | No of incidents |
| --- | --- |
| Accident, Injury |  |
| Contact with object or animal | 3 |
| Contact with or exposure to hazardous substance | 4 |
| Manual Handling - Non patient/service user handling | 1 |
| Slip, trip or fall | 7 |
| Struck against or by an object | 1 |
| Behaviour (including violence and aggression) |  |
| Aggressive/threatening behaviour | 3 |
| Equipment, Devices |  |
| Medical devices | 17 |
| Non-medical equipment | 33 |
| Infection Prevention and Control |  |
| Environmental cleaning (process and procedures) | 5 |
| Infrastructure (including staffing, facilities, environment) |  |
| Cleanliness | 2 |
| Collection/delivery services | 2 |
| Environmental hazards / issues | 6 |
| Vehicles | 2 |
| Total | 86 |

5.0 	RIDDORs

One RIDDOR have been reported to the Health and Safety Executive during quarter one.

The incident took place in the Food, Water and Environment Lab in Glangwilli Hospital, Carmarthen where a staff member was hit by a falling bijou rack of moulded plastic construction after opening a cupboard door. This resulted in the rack striking the individual’s head. First aid was administered onsite. The staff member did not lose consciousness however subsequently went home. Following a return to work, symptoms continued and the staff member attended A & E. An investigation has been undertaken by the Microbiology network Health and Safety Manager which has identified the following actions to prevent future occurrences:

- Identification of obsolete equipment to be removed from all areas to free up space to allow movement of anything stored above average head height of 5 foot to be stored below head height.

- Movement of above head height storage to below head height prioritising heavier objects

- staff training on correct manual handling techniques to be organised immediately through the Health and Safety team

- signage to reinforce correct behaviours

- procurement of additional racking to remove interdepartmental use

- review of departmental work load and resilience

6.0 	Estates Compliance

Over the reporting period 31 March – 30 June 2022 the monitoring and scheduling of compliance has continued to be maintained.   Compliance levels for the five key areas, at sites where the organisation has a statutory responsibility for are shown below.

There are 19 properties within the organisation’s estate portfolio where the responsibility to undertake statutory duties is that of the organisation. These duties include:

- Fire Risk Assessment - 100% compliant

- Asbestos survey/re-inspection – 100% compliant

- Electrical Inspection Condition Report (EICR) – 92% compliant

- Gas Safety Certification – 100% compliant

- Water Management (Legionella) Risk Assessments - 77% compliant

Further details are set out below in relation to electrical inspection condition reports and water management compliance.

Electrical Inspection Condition Report (EICR):  One premise is currently out of compliance as of 31 March 2022.

Magden Park – it should be noted that the inspection has been completed, but a small number of minor recommendations made in the report are still being completed. These recommendations are being managed by local premise lead.

Water Management (Legionella) Risk Assessments:  Three sites are currently out of compliance.

Rhos House (new PHW screening centre) – the site only became operational June 24th and an assessment is currently being scheduled.  It should be noted that water management procedures are in place.

Llys Castan - an assessment has been booked with contractor and confirmation of assessment date is awaited.

Clwydian House – the scheduled assessment has been deferred due to the current renovation works are complete.

The established six year rolling programme of compliance checks continues to be adhered to as far as practicable, so as to ensure inspections and testing are undertaken at appropriate intervals at all sites. Updates will continue to be provided to the group on a quarterly basis providing assurance on compliance.  Challenges, previously reported, with contractor availability for scheduling assessments have reduced.

As previously communicated compliance information is also required to be collated for sites at which we have staff based and for which landlords or host organisations have responsibility for.  An e-assurance document has now been issued to all of our host organisations with a requested completion return date of 30 June 2022. To date, disappointingly only one return has been received providing compliance assurance.  Outstanding responses will be pursued and further return rates will be reported at Q2 reporting.  It should be noted despite the lack of response it should be noted that an assumption should not be made that the hosted sites are not compliant with statutory requirements. If a response is not received we will escalate through the relevant Director of Estates or landlord.

7.0 	Health and Safety Statutory/Mandatory Training

All staff are required to complete a number of statutory and mandatory modules. All directorates are expected as a minimum to attain Welsh Government All Wales compliance target of 85%, with an organisational target of 95%.

The key health and safety statutory/mandatory modules are:

- Fire Safety

- Health, Safety and Welfare

- Moving and Handling Level 1

- Violence and Aggression A

The organisations compliance status for quarter 1 is shown in the table below. There have been small increases in compliance across all four areas Health and Safety training, Manual Handling and Violence and Aggression of training since the last quarter. All four statutory and mandatory training areas remain short of the Public Health Wales target of 95% however Health and Safety and Violence and Aggression training are however meeting the Welsh Government target of 85%.

Table 2: Health and safety training compliance by Directorate (data as of end of June 2022)

| Directorate | Fire Safety % | Health and Safety % | Manual Handling % | Violence & Aggression % |
| --- | --- | --- | --- | --- |
| 028 L3 Corporate Directorate | 60.00% | 80.00% | 84.00% | 68.00% |
| 028 L3 Covid 19 Directorate | 81.52% | 92.39% | 80.43% | 84.78% |
| 028 L3 Data, Knowledge and Research Directorate | 94.06% | 99.01% | 94.06% | 97.03% |
| 028 L3 Health & Wellbeing Directorate | 86.52% | 89.34% | 84.64% | 96.87% |
| 028 L3 Health Protection and Screening Services Directorate | 79.57% | 88.83% | 79.01% | 93.70% |
| 028 L3 Hosted Directorate | 85.29% | 91.76% | 88.24% | 91.18% |
| 028 L3 Improvement Cymru Directorate | 93.83% | 95.06% | 90.12% | 97.53% |
| 028 L3 Operations and Finance Directorate | 90.77% | 90.00% | 92.31% | 96.92% |
| 028 L3 People & OD Directorate | 88.64% | 97.73% | 90.91% | 93.18% |
| 028 L3 Quality Nursing & Allied Profs Directorate | 94.74% | 92.11% | 92.11% | 97.37% |
| 028 L3 SPRs Directorate | 100.00% | 100.00% | 100.00% | 100.00% |
| 028 L3 WHO Collaborating Centre | 92.73% | 98.18% | 89.09% | 98.18% |
| Overall | 83.44% | 90.41% | 83.18% | 93.98% |

Welsh Government target 85%; Public Health Wales target 95%

8.0 Additional training

First Aid / Fire Warden Training

Further to discussion at Health & Safety Group, work has commenced in conjunction with People & OD to review first aid and fire warden requirements and provision across the PHW estate.

The work is focused on defined workspaces, namely Microbiology, screening venues and general administrate areas.  To support the provision of the fire warden training it has been agreed that the organisation will continue to access online training for a further year prior to a return to commissioned classroom based training.  Mandatory requirements relating to first aid training, necessitates that all new /first time trained first aiders are to receive face to face training and therefore further to completion of first aid needs assessments classroom based Emergency First Aid at Work will be purchased for in house delivery.

Working Safely From Home Training

As the Work How it Works Best pilot is run and monitored, and as staff continue to work flexibly and from home, it has been agreed at Health & Safety Group that the organisation will continue to fund all new starters, who wholly or partly work from home, to undertake accredited on line working safely from Home training to ensure their safety and wellbeing.

9.0 	Risk Registers

There are a number of open Health and Safety Risks across the organisation. These are held on Directorate and Divisional Risk Registers. The risks are reviewed by the respective Directorates and by the Divisional Senior Management Team meetings at monthly meetings.

The table below summarises the number of health and safety risks currently managed at a Directorate and Divisional level. Please note this covers all new risks reported since the previous report up until 01 July 2022. Since the last report, two risks have been closed following review. Of the 16 open risks, there are three new risk reported since the last health and safety report. Details of these risks are included below-

| Number of open Health and Safety Risks | 16 |
| --- | --- |
| Number of meeting target risk score (tolerate) | 3 (ID- 987, 1378, 1366) |
| Number of risks not meeting target risk score (treat) | 13 (ID- 978, 980, 720, 1108, 1152, 1169, 1199, 1238, 1241, 1248, 1267, 1345, 1367) |
| New risks since last Health and Safety Report | 1367, 1378, 1366 |

For risks not meeting the target risk score, the Estates and Health and Safety Team continue to work with Health and Safety Leads across the organisation to ensure actions are being undertaken to mitigate the risk down to meet the agreed target score. Work is ongoing with the Chief Risk Officer to explore alternative and improved ways to communicate risks and provide assurance on the action that is being undertaken.

New risk updates:

Risk ID 1367- Microbiology- There is a risk that the main lab room in Llandough may not be able to operate as a result of negative pressure being out of the required range. This may be a result of a new fire door installed in the main corridor. The opening and closing of the door causes the negative pressure to fluctuate however the root cause is still to be determined.

Key controls-

- The negative pressure is checked daily and when staff enter the lab.

- Request has been logged with CC&V Estates for installation of an automatic closer system.

Actions to be undertaken: Further exploration required to determine root cause of the issue.

Risk ID 1378- Microbiology- There is a risk of increased slip/trips/falls associated with ingress of water through the leaking roof. In addition to this, water could cause damage to equipment and potentially damage electrics. This is a result of a number of leaks that NWSSP Estates team are aware of in Lab 2, Imperial Park 5. This can lead to service disruption and potential for continuation in molecular areas.

Key controls-

- Staff make use of spillage pads to absorb water. Rain water is collected in buckets. Staff carry out regular checks during inclement weather to ensure all spillages are adequately dealt with.

- NWSSP Estates have been notified of water ingress on multiple occasions by senior virology staff.

Actions to be undertaken: Continuing to liaise with NWSSP Estates to address issues with the roof and report any new leaks as and when they arise. Work has been undertaken to date but is an ongoing issue.

Risk ID 1366- Microbiology- There is a risk that glass Löwenstein- Jensen (LJ) slopes may break and cause an uncontrolled spillage in the CL3 labs in the WCM at Llandough. The cause is a supply issue with LJ slopes produced by E&O laboratories. LJ slopes are normally supplied in screw-capped polycarbonate containers which are robust and survive drops intact. Due to a global supply issue, E&O had to switch to supplying LJ slopes in glass containers. These are not 100% robust and did not survive drop testing from shoulder height in the laboratory.

The laboratory had a sufficient stock of polycarbonate LJ slopes and have not had to use glass LJ slopes. However, the laboratory receives positive cultures from six laboratories in South West England. We contacted these labs and most of them are using glass LJ slopes. Therefore, the laboratory will receive positive cultures on glass LJ slopes for at least the next 12 weeks.

If a breakage were to occur it could result in a full room fumigation being required. The specific lab affected would be closed for at least one working day causing service disruption.

Key controls-

- Glass LJ slopes are transferred within the WCM in a secure box that provides secondary containment.

- A Bench Aide and Risk Assessment has been published

Actions to be undertaken: Risk to be tolerated and no further action to be undertaken.

10.0 	Alerts and Notifications

The organisation receives a number of alerts under the headings:

- Safety Action Bulletins (SAB)

- Medical Device Alerts (MDA)

- Drug Alerts (DA)

- Chief Medical Officer Alerts (CMO)

- High Voltage Hazard Alerts (HVHA)

- Estates and Facilities Alerts (EFA)

All of these alerts are managed by the Quality, Nursing and Allied Professionals Directorate and a report submitted to the Quality and Safety Committee for information.

The organisation also receives a number of notifications under the headings:

- Specialist Estates Service Notifications (SESN)

- Publication Notices (PN)

These notifications are sent out directly from NHS Wales Shared Services Specialist Estates Service as Specialist Estates Service Notifications (SESN) and Publication Notices (PN) to the Estates, Safety and Facilities Division. For the reporting period, a total five have been received and are detailed in Table 3.

Table 3. Specialist Estates Service Notifications received.

| Date Received | SESN No. / PN No. | SESN Description | Action |
| --- | --- | --- | --- |
| 4/4/2022 | SESNs 2022- 10/11/12/13 | High Voltage Alerts | No action required |
| 6/5/2022 | SESNs 2022- 14/15/16/17/18/19/20 21/22/23 | High Voltage Alerts | No action required |
| 27/5/2022 | SESN 2022-25 | High Voltage Alerts | No action required |

Covid-19 workplace updates

Following the last remaining restrictions regarding the wearing of face masks in health and care settings on 30 May 2022, Public Health Wales has eased all restrictions across its estate however it is at the discretion of individuals if they choose to wear a face covering whilst in our premises. Where we have staff in health board settings, staff are still required to follow local arrangements as required.

Following a review of arrangements and in line with other health boards and the most recent guidance from the World Health Organization (WHO) which makes a strong recommendation that in areas of known or suspected community or cluster transmission, universal masking is recommended in health care facilities. This is also supported by Public Health Wales guidance on managing SARS2-CoV. We have therefore reintroduced measures in order to ensure the continued delivery of our clinical services. We have taken specialist advice from our Infection Prevention Control (IPC) leads and they are supportive of the reintroduction of facemasks in our patient facing clinical areas for both clinical staff and participants as a precautionary measure to reduce transmission at this time in conjunction with usual IPC controls e.g. hand hygiene.  This should also apply if staff are car sharing.  These measures will be in place and continually reviewed until the Covid rate reduces. This does not apply to our offices or non-clinical areas, however all staff can choose to wear face coverings/masks in any setting should they wish.  Staff testing remains unchanged for now, with patient facing clinical staff to continue with twice weekly asymptomatic testing.

At present, a large number of our workplaces are underutilised as staff continue to embrace new and more flexible ways of working which helps us to continue to reduce risk of spread of infection within the estate. Equipment to support staff to work remotely continues to be issued on a case by case basis. This will be reviewed as part of the ‘Work How it Works Best’ trial.

Microbiology update

Containment level 3 sealability issues are ongoing across the estate. Primary cause is an ageing estate which was not purpose built. In house positive pressure testing has been undertaken by H&S team with mixed outcomes. The Bangor Containment Level (CL) 3 laboratory is currently out of use due to required remedial work which is significant. It is being used as a CL2 laboratory but any CL3 work is currently being sent elsewhere within the network. Discussions with health board are ongoing, but previous attempts to seal the room have been unsuccessful.  Currently the contingency in the event of CL3 failure at Rhyl, is to move both the work and staffing across to the Bangor CL3 facility, but this is currently not an option, and there is a need to consider implementing an alternative contingency for Rhyl.

In University Hospital of Wales (UHW) Cardiff, there are also significant issues maintaining certification of sealability this year due to sealability issues with both the main CL3 laboratory and the backup room. Unless substantial remedial work undertaken, this laboratory and its back up will be removed from service next year which will impact on all operational services at UHW including non PHW services. A scoping project is being undertaken working with engineers to provide accurate costings and solutions. . A project request form has been completed and submitted to Cardiff and Vale University Health Board (CVUHB) in order to obtain the room schematics required by the external contractors in order to start to supply this work plan and approximate costings. In addition, a statement of need has been submitted to the Capital Planning Group for the class one safety for replacement. It would be of benefit to tie the projects together to ensure less downtime for the service.

Efficacy studies commissioned of room fumigation have so far been successful at Rhyl and Singleton sites.

The Bangor autoclave is 40+ years old. This has previously been part of a two machine installation, however one machine has been scavenged for parts to keep the second running. This is unsustainable as parts are obsolete. A working group has drafted specifications and identified a preferred supplier to replace both with one machine going forward. This is intended to be submitted with a business case as per previous autoclave replacement projects. This would support the service delivery at Bangor.

There are ongoing issues with University Hospital Llandough estate such that one autoclave is now not in use as the insurance certificate, despite proactive notification, this has not been organised by the CVUHB estates team. This is currently being followed up.

Face masks continue to be mandated for patient facing microbiology staff that are sited in health boards. Currently all health boards are recommending face masks in high footfall areas and certain clinical areas, although it should be noted this is likely to change if covid-19 transmission rises substantially and the microbiology labs will be required to follow the health board guidance if above the PHW requirements.

Reinforced Autoclaved Aerated Concrete (RAACS) update

PHW received from NHS Specialist Estates Service (SES) a Specialist Estates Safety Notice (SESN 22-02 regarding Reinforced Autoclaved Aerated Concrete (RAAC) in buildings constructed between 1960 – 1990 -the notice has been issued further to an alert issued by The Standing Committee on Structural Safety (SCOSS).

The requires PHW to undertake investigations across our estate of all our owned and managed properties for the presence of RAACs.  Further to discussion with SES colleagues we have subsequently been instructed to extend or investigations to include properties where we are either hosted or tenants.

In response to the safety notice instruction the following actions have been undertaken

- A review of the owned and managed estate, 19 properties, has been undertaken to determine properties, which fall within the scope of the affected construction period.

- A structural engineer has been engaged to review the construction details of properties identified as falling within the scope of the notice.

- All landlords and host organisations (Health Boards) where PHW tenants or hosted, 50 properties, have been contacted with a request to provide confirmation as to whether their property falls within the scope of the notice and if so provide confirmation of the status of the presence or otherwise of RAACs.

- A requisite return has been provided to NHS Specialist Estates Service as required detailing the actions PHWE are taking regarding investigations and an update of the position relating to the number outstanding requests from landlords and host organisations.

To date, no RAACs have been identified at any PHW owned or managed properties and only one site where we are hosted has confirmed the presence of RAACs,  however they are not present in a PHW occupied area.

Should any RAACs be identified at any properties where PHW are based or host service users we are required to work with a designated competent person to put in place a management plan to ensure that any risk is appropriately managed by relevant mitigation actions and that management plans are monitored through the corporate risk log.

Summary

The organisation has a number of processes in place for maintaining and monitoring health and safety compliances so that assurance can be provided and any gaps identified with the appropriate actions required.

In light of the risks of Covid-19 transmission we have taken independent health and safety advice, completed risk assessments and reviewed these and addressed actions to ensure our workplaces are Covid safe and continue to monitor compliance and adjust to ensure compliance with regulations. Regular spot checks are taking place and Health and Safety leads are regularly visiting buildings across the estate to address staff concerns and implement actions as necessary. In light of the easing of restrictions, we are in the process of reviewing the remaining restrictions in Public Health Wales.

Incidents and RIDDOR’s are actively managed, with lessons learned identified and shared. Audit schedules are in place, undertaken and results acted upon to ensure gaps in process are resolved. Risk registers have been reviewed with issues identified and actions outlined to mitigate risks.

Processes are in place to monitor policy and procedure reviews and/or development. There are also systems in place to action alerts and notifications as appropriate for the organisation.

The Quality, Safety and Improvement Committee is asked to:

- Note the report; and

- Receive assurance that appropriate actions are being undertaken to address issues raised in this report